# Hardware and software requirements
## Hardware requirements
In order to follow this guide you will need:
- 1 Siemens PLC S7-300 or S7-400 with an MPI interface.
- 1 Siemens MPI Panel
- 1 eWON with MPI port and integrated modem (for example : eWON 2001)
- 2 standard Profibus cables to link the equipments together
- 1 PC with internal or attached modem
## eWON Firmware Version
eWON firmware version 5.6S0 or higher.
A simple way to realize the eWON firmware upgrade is to use eBuddy, the eWON software companion (http://support.ewon.biz).
## Software requirements
eWON configuration software:
The eWON is configured through its embedded web server. So all you need is a standard Web Browser software like Internet Explorer[i] or Firefox[ii].
[i] Microsoft, Internet Explorer, Windows and Windows XP are either registered trademarks or trademarks of Microsoft Corporation
[ii] Firefox is a trademark of the Mozilla Foundation
Additionally we suggest you to download the eBuddy utility on our website :
http://support.ewon.biz
This utility allows to list all the eWONs on your network and to change the default IP address of an eWON to match your LAN IP address range. With eBuddy you can also easily upgrade the firmware of your eWON (if required).

Siemens programming software:
To be able to connect to your S7 PLC and Siemens Panels you need the Step7®[iii] and the WinCC flexible®[iv] software.
[iii] SIMATIC® and STEP7® are registered trademarks of Siemens.
[iv] SIMATIC® and WinCC flexible® are registered trademarks of Siemens.

eVCOM software:
To be able to reach the PLC and the Panel from remote through the eWON you need to install on the PC the eVCOM software. You can download it for free under following link : http://support.ewon.biz/DownloadSoft.html
This software will create a virtual COM port on your PC which will allow you to make the remote maintenance of your MPI devices, as if you where locally connected to the MPI network using the MPI PC adapter cable.
# eWON IP address configuration
Every eWON™ is shipped with the pre-configured IP address 10.0.0.53 and adm/adm as User Name/ Password.
Probably the network settings of your PC does not allow you to connect to the pre-configured IP address.
You can find on our website an utility called «eBuddy» that will allow you to change the IP address of the eWON even if your PC is not on the same IP address range.
eBuddy : http://support.ewon.biz

To change the IP address of your eWON using eBuddy, follow the steps below:
Launch the eBuddy application (eBuddy.exe)

Click on the «Set IP address» link

Enter the eWON serial number in the Serial Number field if you know it, or click on the Browse button. In this case, the dialog box «Select an eWON» will appear showing you all the eWON existing on your Network.

Once the Serial Number entered, click Next.
Set the new IP Address and the Subnet Mask.
Click on Next to launch the update and wait for the eWON to reboot:

When done, click on Finish to exit from the IP Address Wizard.

# eWON configuration for Remote Connection
The remote connection that we will use in this example is a “Direct Phone Connection”. This connection consists in calling the eWON using a standard modem to set up a PPP (point to point) connection. For this, we need to configure the eWON as PPP server. The eWON will then pick up the phone, authenticate the caller and assign an PPP IP address to the eWON and to the PC for the remote connection.
For our example, we will assume to have a layout and address settings as described in the following picture:

NOTE

In this manual we explain the Remote Maintenance using a direct phone connection.
Just keep in mind that with the eWON you can also make Remote Maintenance using other connection types like Internet connection, GPRS connection, VPN connection or using Callback features.

## Accessing your eWON
Accessing your eWON is very simple:
Enter the IP address of your eWON in the address bar of your Web Browser (Internet Explorer, ...): http://10.0.0.53 or http://192.168.0.2 in our example.

On the Connect to pop-up page enter adm (User Name) /adm (Password) then OK.
You are now navigating on your eWON2001.

The menu bar on the top of the main page allows you to navigate through the different display and configuration pages of your eWON.

## eWON PPP connection configuration
The eWON PPP configuration page can be reached on the web page (starting from the main page, see above) following this path:

Configuration → System Setup → Communication →
Network Connections → Modem → Incoming

Check the Server enabled box for the PPP Incoming Connection.
Let the eWON PPP server IP address and the PPP client IP address unchanged. By default the PPP Server address is set to 202.0.0.240.
Enable the protocol compression.
Let the other items unchanged.
Click Update.

# eWON MPI Interface configuration
## eWON IOServer configuration
To configure the eWON MPI Interface, open the S73&400 IOServer settings page by following the path:
Select the S73&400 in the IO Server list. The following page appears:
Configuration → IO Server Config
In the Protocol Type field, choose MPI or Profibus
Set the Baud Rate to the transmission rate of your MPI/Profibus Network (187500)
Set the MPI/Profibus address to the address of your eWON on the MPI/Profibus Network (0)
Set the MPI Highest Station Address in accordance with your MPI/Profibus Network layout (31)
Click the Update Config button at the bottom of the page
Your eWON MPI/Profibus interface is now configured.
## eWON connection on the MPI Network
The MPI port of the eWON is easily identifiable by its blue square surrounding the gender-changer.

Depending on the layout of your MPI/Profibus network, you will have to activate or inactivate the polarization and termination of your eWON on the MPI/Profibus network.
The configuration of the termination and polarization is done by a set of 4 dip switches located on the left side of the eWON housing.
Available dip switch positions:

all dip switches ON

dip switch 1 & 2: ON
dip switch 3 & 4: OFF

NOTE

Bear in mind that on the eWON 2005CD/4005CD series, you do not have to configure dip switches as those models do not have this kind of switches.
## eWON MPI connection verification
To check if the eWON MPI/Profibus interface is correctly configured and connected to your MPI/Profibus network you can reopen the S73&400 IOServer settings page by following the path:

Configuration → IO Server Config
Select the S73&400 in the IO Server drop down list. The following page appears:
Click on the «destination MPI/Profibus Node» link to open the «MPI/Profibus Status Info» pop-up window:

This table will show you the different MPI/Profibus Master devices detected by the MPI chip of the eWON. The detected MPI/Profibus devices are represented with a green square.
If the status table displays only the MPI/Profibus address of your eWON, then the eWON is probably not connected to the network.
If the table doesn't display any MPI/Profibus addresses, then the setup parameters for your eWON are probably not correct. Please check the baud rate settings and verify if the eWON is not using an already occupied MPI/Profibus address.
# Configure eVCOM
To be able to reach the PLC and the Panel from remote through the eWON you need to launch the eVCOM software on your PC. This software will create a virtual COM port on your PC which will allow you to make the remote maintenance of your MPI devices, as if you where locally connected to the MPI network using the standard MPI PC adapter cable.
The eVCOM software can be downloaded under following link
http://support.ewon.biz/DownloadSoft.html

After installation of the eVCOM software, launch the software.

Click on the Add Port button to create a virtual port. The following pop-up window opens:

Select a port and MPI ISOTCP as Port Type, and click on the OK button.

In the Config section of the created port, enter the eWON's IP address as Gateway address and the ISOTCP port configured in the eWON (by default:102) as Gateway Port.
Click on the Update button to validate the configuration

IMPORTANT

As you will connect to the eWON using a dial-up connection you must enter for the Gateway address the PPP IP address of your eWON: 202.0.0.240 (as defined in chapter 3).
You can also use the eWON local IP address if the local PC IP address and the eWON local IP address are not on the same subnet.
When this has been done, click on the Enable Port button to activate the port that you have just created.

The Status area can be used to monitor the status of the eVCOM connection:
- Frame sent and Frame received monitor the exchange between eVCOM and the PG/PC interface.
- TCP sent and TCP received monitor the exchange between eVCOM and the eWON. The Reset statistics button resets the 4 values.
The Last Error field (at the bottom) displays the last error that occurred. The Clear error button can be used to clear the error description, but does not solve the problem!
# PG/PC Interface configuration for the Teleservice
Launch the Siemens Set PG/PC Interface (Simatic Manager/Options) tool in order to configure the way the Siemens has to access the MPI/Profibus equipments.

In the Access Path section, select the PC Adapter (MPI) and click on the Properties button.
In the MPI section, set the Transmission rate to 187.5 Kbps and click on the OK button.

In the Local Connection section, use the Connection to drop-box to select the COM port created with eVCOM and click on OK.
NOTE

Set the Transmission rate to 187.5 Kbps even if your MPI/Profibus Network uses an other transmission rate.

Now the Siemens softwares (Simatic Step7®, WinCC flexible®) will be able to access the MPI network.

NOTE

PROFIBUS Network: if you want to connect to a Profibus network, the S73&400 IOServer of the eWON must be configured in PROFIBUS but all the above steps are exactly the same as for MPI.
So even if eWON is connected to a Profibus network you must still choose the PC Adapter (MPI) for the PG/PC Interface.
# Establish the remote connection
On your PC you will need to create a dial-up connection.
You can create a standard dial-up connection in Windows using the «New Connection Wizard» or you can use eCatcher, a free downloadable program on our Website.
With eCatcher you can create and manage easily your different remote connections. Among other things, with eCatcher you can configure your dial-up connection to launch automatically the corresponding Step7® project once the dial-up connection established.
eCatcher : http://support.ewon.biz/DownloadSoft.html

## Using the Windows Dial-up connection
Click on your dial-up connection to open the «Connect» window:
In the User name and Password fields enter a valid eWON user name and password (adm/adm for example)
Enter the phone number of the eWON to call and click on the Dial button.

Once the connection is established, the status of your Dial-up connection becomes «connected».
## Using eCatcher
To create a new Dial-up connection in eCatcher follow these next steps:
Launch the eCatcher application (eCatcher.exe)
Select the «My connection» tab (not the Talk2M tab).
Click on «Add a Dial-up entry»
On the Dial-up tab, enter the following information:
Name: a name to identify the Dial-up connection
Connect using: choose the Modem that you will use on your PC
Phone Number: enter the phone number of your eWON. You can use or not the dialing rules defined on your PC.
Login: enter a valid eWON user and password (adm/adm for example)

Go to the Notes tab:
This window will allow you to encode some information that will be useful for the remote connection. For example, the name of the involved Step7® project or the addresses of the PLC which can be reached through the remote connection, ...

Go to the Action tab:
This window will allow you to configure the action that will be performed once the remote connection is established.
You can choose No Action or for example define to start automatically Step7® with the concerned project. To realize this, configure the Action settings like following:
Action performed upon connection: Start an external program
Program filename: Use the «...» button to chose the Step7® program (S7tgtopx.exe)
Program arguments: /e & full path of your Step7® project
( for our example: /e "c:\program files\siemens\step7\s7proj\ewon_mpi\ewon_mpi.s7p"
Click OK to close the Properties window.

The Dial-up connection that you have created will now appear in the list of «eWONs -Dial-up».
To start the remote connection follow the steps below:
Double-click on the eWON – Dial-up you want to open (Company XXXX – Production YYYY)
Click on the Dial button to start dialing.
Once the PPP connection is established, the Step7® project will start automatically.
In eCatcher, the active Dial-up connection will be checked in green color and the Status column will indicate the PPP server address (Connected: 202.0.0.240).

# Remote Maintenance
## PLC Connection
Open the Simatic Step7® software to perform maintenance of your PLC's.
Once the telephone connection established, you can connect to your PLC as if you were connected directly to the PLC using the PC adapter cable.
### View the available nodes
To view the available nodes, click on the Accessible Nodes icon.

### Upload a Project
In Simatic Step7® select the PLC/ Upload Station to PG... feature.

The following page opens:
Click on the View button to display the MPI master nodes of the network.

Select an MPI address and click on OK button.

The project is being uploaded:

### Download a Project

Open your project:
The following window will be displayed:

To download your project, select the PLC device and click on the Download button.

### Online Viewing
Open your project and under the View menu select the Online option.

You can now work online on your project.
## MPI Panel
Open the WinCC flexible® software to perform the maintenance of your MPI Panels.
Once the telephone connection established, you can connect to your Panels as if you were connected directly to them using the PC adapter cable.
### Backup a project
Open the communication settings window.

For the communication Mode select MPI/DP, and enter the Station address of your Siemens Panel (5, in our example).
Click on OK.
You should now be able to Backup you project from remote.

### Transfer a Project
Open your project and select the Transfer settings window
In the Transfer window set the Mode to MPI/DP, and enter the Station address of your device (5, in our example).
Click on the Transfer button to start the transfer.

# eVCOM Limitations
eVCOM only allows to access to 1 MPI device on the same time.
So you cannot for example monitor real time data simultaneously on 2 PLCs.
On the same way, you cannot monitor real time data on 1 PLC using Step7® and download a project to an MPI Panel at the same time. You will first need to close the online connection in Step7® to be able to download the project into the MPI panel using WinCC flexible®.