Use of Topics for Tag Polling
For each I/O Server, there are 3 topics (A, B, C) that you can define. In those topics you can choose the frequency of polling. You can also specify on which equipment you would like to read the linked Tags.
If you do not specify the destination equipment in the Topic, then you can specify the destination in the Tag. This way, you are able to reach more than 3 PLCS.
Hereunder an example of Destination addresses specified in the Tag:

In the above example, the Register DB1W2 will be read on MPI, 6; if the destination address is not specified at Topic B.

In this case, the Register DB1W2 will be read on MPI, 7; if the destination address is not specified at Topic B.

Let us assume that you have configured your eWON like this:
I/O Server Configuration
In the following picture, the Topics A and B have been enabled. This means that for this I/O Server, the eWON will apply those parameters for each Tag linked to the 2 different topics. As you can see in our example, the Topic C has an address and a poll rate. But, as it has not been enabled, the Tags linked to this topic will not be polled.

Attention: the Topic B has been enabled but has not been linked to any PLC (Global Device Address is empty). So, the Tag(s) linked to the Topic B will be polled every 2000 ms, but you will have to specify the PLC address in each Tag that you want to link to this topic (as mentioned before).

Tag Configuration
In the following picture, you can see a list of Tags created in the eWON. As you can see all of them are linked to a Topic (A, B or C).

So for example, Tags DB1W0 and Q0#0 will be read on the device MPI,6, every 1000 ms. The MPI,7 at the end of the IO address of Tag DB1W0 will not be taken into account, because if the destination address is also mentioned in the Topic, the destination address specified in the Tag will be ignored.
On the other hand, Tag DB1W2 will be polled every 2000 ms on MPI,6 as specified during the setup of this Tag (since we have not introduced any device address in the Topic B).
The same occurs with DB1W2_PLC_7. It will be polled every 2000 ms on MPI, 7 as defined in the Tag setup.
Finally, Tag DB1W4 will not be polled as the Topic C has not been enabled.