Schneider M340
Communications tests
# Schneider M340
Tests made on M340 (provided by EFA).
Power: CPS2010
CPU: P3420102 (CanOpen + Serial)
Ethernet: NOE0100

Software used: UnityProS (evaluation period of 21 days)
## Ethernet link
The Ethernet plug is an RJ45 marked with a green arrow.
Device was received with the IP: 192.0.0.242
First connection was made with this address.
Software used: UnityProS
On Unity, goes on menu
PLC->Set Address

And copy the program on Unity (Upload Project).

### Ethernet Remote Maintenance

Test made with Talk2M Free : routing through an eWON2005 on Internet on WAN : OK

## Serial link
The serial connector is a RJ45 plug (marked with a black arrow).

RJ45		eWON-DB9
4 (D1)	---------	3 (A+)
5 (D0)	---------	8 (B-)
8	---------	5

Modbus RTU (RS485) configuration of the M340:
Goes on the SerialPort configuration of the M340 and set the ModbusRTU parameters to what you need:
Function	Modbus link
Type	Slave
Slave number	2 (for example)

Build and download the project to use your new settings.
Test your settings by polling Modbus tag (ex: 40001) from an eWON.

### Serial Remote Maintenance
As the M340 is Modbus, Serial Remote Maintenance will be done with the Modbus gateway (ModbusTCP → ModbusRTU) functionality of the eWON.

Create a ModbusTCP eVCOM port:

and configure the Schneider Serial modbus Driver to use the eVCOM port (here COM5).

and set the Unity communication settings to Modbus and Address 2
Disable the Speed auto-adaptation.

# Remote Maintenance tests
## Ethernet link with M340
eWON2005 Internet on LAN	eCatcher Free	OK
eWON2005 Internet on ISDN	eCatcher Free	OK
eWON2101 Internet on EDGE	eCatcher Free	OK (*)
eWON2101 Internet on GPRS	eCatcher Free	OK (*)

## Serial link with M340
eWON2005 Internet on ISDN	eVCOM + eCatcher Free	OK
eWON2101 Internet on EDGE	eVCOM + eCatcher Free	OK
eWON2005 Internet on GPRS	eVCOM + eCatcher Free	OK

(*) I've encountered some connection errors/retries.
Then I increased the TimeOut to 10sec (default is 3sec) and the communication was more reliable.